Check on the problem you meet with diesel engine, alternator and electrical control, find the causes and remedies for the problem. 根据动力，电机，机组与控制模块相对应的问题，寻找相关解释. 1.Diesel Engine. - Faults on Fuel Valve 1.2.Low compressive pressure 1.3.Too High Air Press Inside Crank Box 1.4.Wear of Piston, Piston Ring, Bearing, and Axle Journal , including,Cylinder Packing 1.5.Engine Decoupling 1.6.Engine Vibrates 1.7.Engine Running Unstably 1.8.Too Large Lub. Oil Consumption Rate 1.9.The engine knocking cylinder 1.10.The consumption of fuel excels the normal level 1.11.The Temperature of Coolant Below the Normal 1.12.Too High Pressure of Lubricant Oil 1.13.Too low lub. Oil pressure 1.14.Insufficient Output 1.15.The engine unable to stop 1.16.The engine cannot reach the rated rotary speed 1.17.Emitting blue smoke or white smoke 1.18.Emitting black smoke 1.19.The engine can start but cannot keep running 1.20.May turn the engine but cannot start, without smoke from the exhaust pipe 1.21.The engine has the start difficulty or cannot start, gives off black smoke 1.22.The engine cannot be turned or only be turned slowly - 动力 1.1输油管路问题 1.2油压低 1.3曲轴箱体气压过高 1.4活塞套，活塞环，轴承，轴颈，气缸全件套 1.5动力去耦 1.6 动力摆动 1.7动力运行不稳 1.8润滑液消耗量过大 1.9气缸震动 1.10燃油消耗过大 1.11冷却液温度低于正常值 1.12机油压力过高 1.13机油压力过低 1.14功率输出不足 1.15动力无法停机 1.16无法到达额定转速 1.17冒蓝烟白烟 1.18冒黑烟 1.19可以启动，但启动之后无法正常运行 1.20 启动时动力转动，但是无法正常启动，且排气管无排烟 1.21很难启动或者无法启动，冒黑烟 1.22无法停机，或者停机速度过慢. 2.Alternator. 2.1.Too low voltage of the genset under a load 2.2.Too low voltage at free running of the genset 2.3.Too High of Output Voltage 2.4.Unstable Output of Voltage of the Genset 2.5.During running of the genset, no voltage outputs 2电机 2.1带负载时低电压 2.2无负载时低电压 2.3输出电压过高 2.4，电压不稳 2.5机组运行时，无电压输出. 3.ElectricaI Control. 3.1.Remote Emergency Stop Cannot Be Realized 3.2.Remote Monitor Cannot Be Realized 3.3.Automatic stop function failure 3.4.Unable to stop manually 3.5.The genset unable to undertake load 3.6.Low Voltage Alarming 3.7.High Voltage Alarming 3.8.Stop Of Over Speed Fault 3.9.Low Oil Pressure Faults Alarming/Stop 3.10.High Water Temperature Faults Alarming/Stop 3.11.In case of the start motor running, the genset unable to couple 3.12.In case of the signal"START" correctly input, but manual /auto unable to start 3.13.Key start failure 3电器控制部分 3.1急停开关无法遥控 3.2控制屏无法遥控 3.3自动停机功能失灵 3.4无法手动停机 3.5无法带负载 3.6低油压报警 3.7高水温报警 3.8过转停机 3.9机油压力过低报警或者停机 3.10高水温报警或者停机 3.11启动马达运行，机组却无响应 3.12启动信号输入，机组无启动 3.13手启动失败. 1、DIESEL ENGINE. 1.1.Faults on Fuel Valve Check Methods: A. Voltage of fuel valve. B. Suction iron clicks C. Overflow valve. A. In case of the key switch at the working position, the connection point of magnetic valve shall has voltage under the working conditions, the purple wire shall have voltage, the coil consumes power of 24W, in case of 24V, current of approx. 1A, the black wire is of negative. B. Movable diesel engine. Tell the assistant to turn the key switch to the working position, then turn to O position, the valve will give off click, if necessary, check the action of iron, dot press the start button and the stop button in turns, the valve will give off click.(Repeat if necessary). C. Check if the overflow valve can be sealed negatively, if not, replace the overflow valve 1.动力 1.1然后管路问题 需检查内容 - 有关压力 - 吸铁点击 - 满溢阀 <--TOP 1.2.Low compressive pressure Causes: A. Block of air filter or the air inlet system. B. Improper gap of air door. C. Mistaken timing of distribution. D. Air leakage of cylinder liner. E. Air door open and close inflexibly. F. Wear of cylinder packing. G. Air leakage between air door and air door base. H. Friction, wear, or break of piston ring. I. Wear of air door rod and/or air door conduit. J. Break of air door spring. Remedies: A. Replace air filter /clean the air inlet system. B. Check/adjust gap of air door. C. Adjust as per the stipulated data. D. Refer to the manual for measuring surface degree or replace cylinder liner. E. Clean, replace, or regrind air door. F. Shown on wear of piston, piston ring, bearing, and axle journal. G. Replace/regrind air door and air door base. H. Replace piston ring. I. Replace air door and air door conduit. J. Replace air door spring. 1.2压力过低 原因分析： - 空气滤清或者进气管道堵塞 - 气门箍规格不对 - 进气时间错误 - 缸体漏气 - 气门无法正常 开合 - 气缸套问题 - 气门与气门连接处口气 - 活塞环磨损，损坏或堵塞 - 气门导管堵塞 - 气门弹簧损坏 解决方法： - 更换空滤，清理进气口 - 检查气门卡箍 - 调校相关参数 - 测量动力表面温度，或者更换汽缸套 - 清理或者更换气门 - 检查活塞套，活塞环，轴承，轴颈，气缸全件套 - 清理或者更换气门或气门座 - 更换活塞环 - 更换气门管 - 更换气门弹簧 <--TOP. 1.3.Too High Air Press Inside Crank Box Causes: A. Block of vent pipe. B. Wear of cylinder packing. C. Friction, wear or break of piston ring. D. Wear of air door rod and/or air door conduit. E. Damage of piston. <--TOP. Remedies: A. Check if the vent pipe is blocked. B. Shown on"wear of piston, piston ring, bearing, and axle journal". C. Shown on"wear of piston, piston ring, bearing, and axle journal ". D. Replace air door bar and/or air door conduit. E. Shown on"wear of piston, piston ring, bearing, and axle journal". 1.3曲轴箱气压过高 原因分析： - 排风管堵塞 - 汽缸堵塞 - 活塞环堵塞，或者损坏 - 气门或者气门导管堵塞或损坏 - 活塞损坏 解决方法： A.检查排风管是否堵塞 B.检查活塞套，活塞环，轴承，轴颈，气缸全件套 C.更换气门或者气门导管 1.4.Wear of Piston, Piston Ring, Bearing, and Axle Journal , including,Cylinder Packing Causes：. A. Air leakages between the air filter and the turbocharger. B. Too high sulfuric contents in fuel. Remedies： <--TOP. - Replace parts if necessary, ensure there is no leakage. - Check specification of fuel/ contact with the fuel supplier. 1.4活塞、活塞环、轴承和气缸套 原因分析： A.在空气过滤器和涡轮增压器之间漏气 B. 燃油含硫量过高 解决办法： - 更换部件确保不泄露 - 与燃油供应商确认燃油参数 1.5.Engine Decoupling Causes：. A. Pull -- rod of throttle. B. Air in the oil inlet passage. C. Friction of high speed movement of the speed adjustor. Remedies： <--TOP. - Check if the gap of connect pints of the pull -- rod is too large, adjust for correct gap, replace component if necessary. B. Check if there is leakage, replace the damaged parts. C. Repair the speed adjustor, replace if necessary. 1.5动力去耦 原因分析： A.节流孔标尺错误。 B. 空气在燃油油入口段落。 C. 调速器的高速运动的摩擦。 解决办法： A. 检查空白是否连接拉扯的品脱 -- 标尺是太大，调整为正确空白，如果需要替换组分。 B. 替换损坏的零件，检查是否漏液。 C. 修理调速器，如果需要的话替换。 1.6.Engine Vibrates Causes：. A. Faults on oil injector or improper type. B. Friction of control system of rotary speed. C. Too high temp. of engine. D. Damage of cooling fan. E. Assemble faults of engine. F. Faults on oil inject pump. G. Low compressive pressure. H. Adopt wrong HP pipes or installed mistakenly. l. lmprover alignment of bell housing and flywheel. Remedies： <--TOP. A. Check, adjust or repair oil injector or select correct type. B. Check, clean. C. Check, add coolant, inspect fan, thermostat, check water leakage. D. Repair fan. E. Contact with the authorized repairman. F. Ask agent to check the oil inject pump. G. Shown on "low compressive pressure". H. Replace or correct. I. Contact with agent.. - 动力震动过大 原因分析： A. 燃油喷射器问题或型号不匹配。 B. 转台式速度控制系统的摩擦。 C. 太高温。 引擎。 D. 冷却风扇损伤。 E. 装配引擎缺点。 F. 缺点在油注射泵浦。 G. 低压缩压力。 H. 采取错误HP管子或错误地安装。 I.飞轮与气缸校正 解决办法： A. 检查，调整或修理油注射器或选择正确类型。 B. 检查，干净。 C. 检查，增加蓄冷剂，检查风扇，温箱，检查水漏出。 D. 修理风扇。 E. 联络与授权安装工。 F. 请求代理检查油注射泵浦。 G. 显示 H.更换或者校正 I.咨询代理商 <--TOP. 1.7.Engine Running Unstably Causes： A. Block of fuel pipe. B. Fault on oil transfer pump. C. Dirty filter for fuel oil. D. Improper adjust/assembly of spring of speed adjustor. E. Fault of oil injector or wrong type. F. Block of ventilation of fuel tank. G. Air in the fuel system. H. Block of air filter or wrong type. I. Friction of rotary speed control system of engine. J. Too high temp. of engine. K. Improper gap of air door. L. Excess lub. Oil or improper brand of oil. M. Faults on cold start system. N. Block of the exhaust pipe. O. Faults on oil injecting pump. P. Low compressive pressure. Q. Friction of air door. R. HP oil pipe selected or installed mistakenly. S. Break of spring of air door. Remedies： A. Check/replace fuel pipe. B. Check/repair oil transfer pump, replace if necessary. C. Replace filter for fuel oil. D. Adjust /replace spring of speed adjustor. E. Check/adjust or replace oil injector. F. Clean/install pipes of ventilation. G. Remove air in the fuel system. H. Replace air filter/ensure correct type. I. Check, clean. J. Shown on"temp. of coolant above the normal". K. Check/adjust gap of air door. L. Check and adjust oil volume or replace with correct kind and type. M. Install cold start supplement set. Check, repair cold start set, replace if necessary. N. Check and remove block, ensure correct size of the exhaust pipe. O. Contact with local agent. P. Shown on "low compressive pressure". Q. Clean rod of air door and hole of conduit. R. Correct or replace. S. Replace spring of air door.. 1.7.运行不稳定。 原因分析： A.油管堵塞 B在输油泵故障。 C .肮脏的滤油器。 D .不当调整/组装速度调节器弹簧。 E油故障注入器或类型错误。 F .块通风的燃料箱。 G .燃料空气系统。 H .块空气过滤器或类型错误。 我摩擦旋转速度控制引擎系统。 J .温度过高。发动机。 K .不当的差距空气门。 属多余的润滑。油油或不当的品牌。 米冷启动系统故障。 北块的排气管。 O .故障注油泵。 体育低压缩压力。 问：摩擦空气门。 R .惠普油管选定或安装错误。 解决办法： A. 燃料阻塞管子。 B. 缺点在输油泵。 C. 肮脏的过滤器为燃料油。 D. 不正当调整或速度调整器的春天装配。 E. 油注射器或错误类型缺点。 F. 汽油箱的透气块。 G. 空气在燃料系统。 H. 空气过滤器或错误类型块。 i. 引擎转台式速度控制系统的摩擦。 J. 太高温。 引擎。 K. 空气门不正当的空白。 L. 剩余lub。 油或油不正当的品牌。 M. 缺点在冷起动系统。 N. 排气管的块。 O. 联络与地方代理。 P. 显示 Q. 清洗空气门输送管道标尺和孔。 R. 改正或替换。 S. 替换空气门的春天。 <--TOP. 1.8.Too Large Lub. Oil Consumption Rate Causes： A. Wear of bearing and sealing ring of turbocharger. B. Break or wear of piston ring. C. Wear or damage of cylinder packing and piston. D. Improper brand of lub. Oil. Remedies： A. Repair/replace turbocharger, check lub. Oil. B. Replace cycle shown on"wear of piston, piston ring, bearing, axle journal". C. Shown on"wear of piston, piston ring, bearing, axle journal". D. Replace lub. Oil/ filter, ensure adoption of proper lub. Oil.. 1.8.润滑油，燃油消耗量过大 原因分析： A. 轴承和蒸气增压器密封圈穿戴。 B. 活塞环断裂或穿戴。 C. 佩带或圆筒包装和活塞损伤。 D. lub不正当的品牌。 油。 解决办法： A. 修理或替换蒸气增压器，检查润滑油。 B .更换周期显示在“磨损的活塞，活塞环，轴承，轴颈”。 C .显示在“磨损的活塞，活塞环，轴承，轴颈”。 D .更换润滑。油过滤器，确保通过适当的润滑油。 <--TOP. 1.9.The engine knocking cylinder Causes： A. Faults on oil Transfer pump. B. Fault on oil injector or improper type. C. Faults on the cold start system. D. Apply mistaken type or brand of fuel. E. Improper adjust of control rod of throttle. F. Too high temp. engine. G. Improper gap of air door. H. Excess lub. Oil or mistaken spec. of lub. Oil. I. Air leakage of oil suction pipe. J. Improper timing of oil supply. K. Friction of air door. L. Low compressive pressure. M. Wear or damage of crank bearing. N. Break of spring of air door. Remedies： A. Check/ repair transfer pump, replace if necessary. B. Check/adjust or replace oil injector. C. Install the cold start set, check, repair, replace if necessary. D. Apply super diesel with low sulfur content, max. of 0.05%. E. Check strokeof throttle. F.Shownontemp. of engine excels the normal±. G. Adjust/check gap of air door. H. Refer the manual for correct volume and spec. I. Check leakage, replace the faulted parts. J. Check the set data and adjust oil injector. K. Clean/replace or regrind air door. L. Shown on"low compressive pressure". M. Replace crank bearing, check replace cycle. N. Replace spring of air door.. 1.9.发动机敲缸 原因分析： A.断层对油输送泵。 B .故障或不当式喷油器。 C .故障对冷启动系统。 D .申请错误的类型或品牌的燃料。 E不当调整油门控制杆。 F .温度过高。发动机。 G .不当的差距空气门。 H .多余的润滑。油或错误的规格润滑。油。 我漏风的吸油管。 J .时机不当石油供应站。 K .摩擦空气门。 属低压缩压力。 M磨损或损坏曲轴轴承。 2 .打破春天空气门。 补救措施： 检查/维修输送泵，必要时更换。 B .检查/调整或更换喷油器。 C安装冷启动，检查，修理，必要时更换。 D .柴油硫含量低，最大0.05%。 E.检查缸体节流阀。 F.发动机比正常±。 G.检查间隙调整风门。 H .参考手册正确的数量和规格。 I检查泄漏，更换断裂零件。 J .检查设置的数据和调整喷油器。 K .清洁/更换或再生空气门。 M研究显示在“低压力”。代替曲柄轴承，更换周期检查。 N .更换空气门弹簧。翻译结果重试 抱歉，系统响应超时，请稍后再试 - 支持中文、英文免费在线翻译 - 支持网页翻译，在输入框输入网页地址即可 - 提供一键清空、复制功能、支持双语对照查看，使您体验更加流畅 <--TOP. 1.10.The consumption of fuel excels the normal level Causes： A. Block of the air filter, or wrong type. B. Block of the oil injector, or wrong type. C. Too low temperature of engine. D. Improper gap of the air door. E. Faults or improper setup Of the pressure adjustor. F. Improper timing of oil supply. G. Improper adjustment of the oil control rod. H. Thin air owing to too high ambient temp. or altitude. I. Overload of engine. J. Fuel leakages inside or outside. K. Friction Of ventilation of the fuel box. L. Friction of the exhaust pipe. M. Faults on the cold start system. N. Friction of air door. O. Low compressive pressure. Remedies： A. Find out causes/ replace if necessary. B. Check/adjust or replace the injector. C. Shown on "temp.of coolant below normal temp". D. Adjust/check gap of the air door. E. Repair/readjust. F. Check the data of the injector and adjust. G. Check full stroke of throttle. H. Modify as the sales manual of engine. I. Check max. load, decrease if necessary. J. Removal of leakages. K. Clean /add vent pipe. L. Inspect friction of the exhaust pipe and proper size. M. Install the cold start set, check, repair, and replace if necessary. N. Clean/replace or regrind air door. O. Shown on "Low compressive pressure".. 1.10.燃料消耗量超过正常水平 原因分析： A空气过滤器堵塞，或类型错误。 B块的喷油器，或类型错误。 C .太低温发动机。 D .不当的差距空气门。 E .错误或不当安装的压力调节器。 F .时机不当石油供应站。 G .不当调整油控制杆。 H .稀薄的空气由于环境温度太高。或高度。 I.超负荷的发动机。 J .燃料泄漏的内部或外部。 K .摩擦通风的燃料箱。 L摩擦的排气管。 M.断层对冷启动系统。 N .摩擦空气门。 O低压缩压力。 解决办法： A .找出原因/必要时更换。 B .检查/调整或更换喷油器。 C .显示在“temp.of冷却低于正常温度”。 D .调整/检查间隙的空气门。 E.修复/调整。 F .检查数据的注射器和调整。 G .检查全行程节流阀。 H .修改发动机销售手册。 I.检查的最大负荷，减少必要的话。 J .消除泄漏。 K .清洁/添加排气管。 L .检查摩擦的排气管和适当的大小。 M.安装冷启动，检查，修理和更换，如果必要的话。 N清洁/更换或再生空气门。 O上显示“低压力”。 <--TOP. 1.11.The Temperature of Coolant Below the Normal Causes： A. Too low level of coolant. B. Block or damage of the heat radiator. C. Dent or block of flexible pipe of the heat radiator. D. Loose driving belt of fan. E. Improper level of lub. Oil. F. Damage or lose of cover of cooling fan. G. Problems concerning pressure cover of the radiator or mistaken type. H. Problems concerning the temperature meter. I. Shuttering of the radiator was not fully open. J. Block or mistaken type of air filter. K. Faults of oil injector or mistaken type. L. Block of the exhaust pipe. M. Damage of fan. N. Block of water or air passage of the radiator. O. Insufficient coolant in the system. P. Accumulated air in the cooling system. Q. Faults with the water pump. R. Faults / mistake type of thermostat. S. Air in the cooling system. T. Faults on the oil injecting pump. U. Mistaken timing of oil supply. V. Improver valve timing. W. Leakage of cylinder liner. X. Damage of piston. Remedies： A. Add coolant. B. Clean as per the Manual, repair if necessary. C. Inspect flexible pipe, replace if necessary. D. Inspect the tightening degree of the belt, tighten. E. Add or drain off lub. Oil, check mark of oil scale. F. Check the cover of the fan, repair, replace, or reinstall. G. Check the pressure cover, replace if necessary. H. Check/repair the temperature meter, replace if necessary. I. Check/repair shuttering, replace if necessary. J. Check or replace the air filter. K. Check/adjust or replace the oil injector. L. Check block of the exhaust pipe, inspect sizes. M. Replace fan. N. Check and clean. O. Add coolant. P. Remove the air in the cooling system. Q. Check/repair, or replace the water pump. R. Check/replace thermostat. S. Check leakages of flexible suction pipe, leakage of cylinder cover. T. Ask agent to inspect the oil injecting pump. U. Consult data of fuel injecting pump, adjust. V. Adjusted as per the stipulated data. W. Check cylinder liner. X. Replace cylinder packing and piston. Find out the causes of damage.. 1.11.the冷却液温度低于正常值 原因分析： A水平太低的冷却液。 B .堵塞或损坏的散热器。 C .凹痕或块柔性管的散热装置。 D .松皮带驱动风扇。 E不当的滑。油。 F .损坏或丢失的冷却风扇罩。 G .有关问题的压力盖散热器或错误的类型。 H .有关问题的温度仪表。 I模的散热器是不完全开放的。 J .块或错式空气过滤器。 K故障或错误式喷油器。 L排气管堵塞 M损伤的。 N块的水或空气通过散热器。 O不足冷却剂系统。 P积累空气在冷却系统。 Q：与水泵故障。 R .故障/错误类型的温控器。 S.冷却系统。 T故障注油泵。 U.燃油供应。 V改进剂气门正时。 W泄漏的气缸套。 X.损坏活塞。 解决办法： A .添加冷却液。 B .清洁按手册，如果需要进行修理。 C.查软管，必要时更换。 D.检查的松紧程度带，紧固。 E.如添加或排出润滑。油，检查标记的油量表。 F .检查盖板的风扇，修理，更换，或重新安装。 G .检查压力盖，必要时更换。 H .检查/维修表温度，必要时更换。 I.检查/修复模板，必要时更换。 J .检查或更换空气过滤器。 K检查/调整或更换喷油器。 L.校验块排气管，检查尺寸。 M .更换风扇。 N.检查和清洁。 O .添加冷却液。 P去除空气中的冷却系统。 Q：检查/修复，或更换水泵。 R .检查/更换温控器。 S.检查泄漏柔性吸管，泄漏的气缸盖。 T.检查喷油泵。 U.参考数据调整燃油喷射泵。 V.调整为每规定的数据。 W .检查气缸衬垫。 X.更换气缸和活塞包装。找出造成损害。 翻译结果重试 抱歉，系统响应超时，请稍后再试 - 支持中文、英文免费在线翻译 - 支持网页翻译，在输入框输入网页地址即可 - 提供一键清空、复制功能、支持双语对照查看，使您体验更加流畅 <--TOP. 1.12.Too High Pressure of Lubricant Oil Causes： The pressure reducing valve unable to open. Remedies: Replace the pressure reducing valve. 1.12.机油压力过高 原因分析： 减压阀无法打开。 解决办法： 替换减压阀. <--TOP. 1.13.Too low lub. Oil pressure Causes: A. Improper level of lub. Oil. B. Problems on the pressure meter of lub. Oil C. Lub. Oil diluted by fuel. D. Mistaken brand of lub. Oil. E. Lub. Oil temp. excels the normal (120). F. Dirt of the filter for lub. Oil. G. Wear or damage of crank bearing. H. Wear of lub. Oil pump. I. Open of pressure reducing valve. J. Damage of the pressure reducing valve. K. Faults on the suction pipe of lub. Oil pump. L. Block of suction filter of oil sump. Remedies: A. Check leakage of lub. Oil, add or drain off. B. Check engine oil scale. C. Check lub.oil pressure meter. D. Replace lub.oil . If diluted once again,contact with the authorized office. E. Replace lub.oil temp, check brand. F. Check, clean, or replace lub.oil cooler. G. Replace lub.oil filter. H. Inspect/replace crank bearing. I .Inspect, repair/replace lub.oil pump. J .Replace the pressure reducing valve. K.Replace the pressure reducing valve. L . Inspect, repair/replace suction pipe suction pipe,clean filter. 1.13.机油压力过低 原因分析： A：润滑油标号过低 B .问题上的压力表润滑油 C .润滑油燃料油稀释。 D .错品牌润滑油。油。 E.机油温度。擅长正常（120）。 F .污垢的过滤器润滑。油。 G.曲柄轴承磨损或损坏。 H .磨损润滑。油泵。 I.打开减压阀。 J .损坏减压阀。 K故障的吸管滑。油泵。 L．机油滤清堵塞 解决办法： A.检查泄漏的润滑油，添加或排水。 B .检查机油标尺。 C.检查润滑油压力表。 D .更换润滑油。 E .检查品牌。 F .检查，清洁，或更换机油冷却器。 G .取代机油过滤器。 H .检查/更换曲轴轴承。 I.检查，修理/更换机油泵。 J.更换减压阀。 K .代替减压阀。 L检查，修理/更换吸管吸入管，清洗过滤器。翻译结果重试. <--TOP. 1.14.Insufficient Output Causes: A. Too large load considering of rated power. B. High altitude causes insufficient power. C. Block of fuel pipe. D. Too high lub. Oil level. E. Obstacle to move of control rod of thrott1e. F. Block of air inlet and outlet system. G. Air in fuel -- bubbles in the oil passage. H. Block of oil return pipe or unsmooth ventilation of oil tank. I. Improper gap of air door. J. Applied wrong type or brand of fuel. K. Too high temp. of air inlet (over 40). L. Too low temp. of air inlet (below 0). M. Too high temp. of fuel (over 70). N. Fault on the fuel injector or wrong type of injector. O. Faults on the supply pump. P. Dirt of the fuel filter. Q. Too high friction of speed adjustor, fault or wrong setup. R. Fault or wrong setup of pressure adjustor. S. Too low setup of max. speed limit of the speed adjustor. T. Fault on the fue1 injecting pump. U. Mistaken timing of oil supply. V. Low compressed pressure. W. Damage or dirty of wheel of turbocharger. X. Abnormal working of air door (if installed). Remedies: A. Lower loads. B. Adjust the engine in case of the altitude of over l000 meters. C. Check block of fuel lines. D. Check oil scale and volume of oil sump. E. Check position of the control rod if full open of throttle. F. Check bock of air inlet and outlet system. G. Remove air in fuel, tighten pipe joints and filter. H. Check vertical pipe of oil tank. I. Check bock, torsion, or dent of oil return pipe. J. Check and adjust gap of air door. K. Apply a temporary oil tank to start engine for identification. L. Introduce air to supercharger when high air temp. M. Introduce air under casing to engine when low tem. N. Fill oil tank, stop of fuel heater, max. temp of 70. O. Check/ speed adjust, or replace the oil injector. P. Check, repair the oil transfer pump, replace if necessary. Q. Replace the fuel filter. R. Contact with the authorized personnel. S. Contact with the authorized personnel. T. Check/adjust the speed adjustor. U. Ask agent to check oil injecting pump. V. Consult data of fuel injecting pump, adjust, shown on "Low compressive pressure". W. Clean, repair or replace turbocharger. X. Find out causes, clean, repair, or replace air door. 1.14输出功率不足 原因分析 - 过载 - 海拔过高导致功率损耗 - 输油管路堵塞 - 机油压力过高 - 控制绡堵死 - 进气或者排气系统问题 - 燃油进 - 机油油路堵塞 - 进气门问题 - 燃油标号不对 - 进气温度过高 - 进气温度过低 - 燃油温度过高 - 喷油泵问题 - 燃油嘴问题 - 柴油滤芯问题 - 调速器速度设置过快 - 油压调节错误 - 调速器速度设置过慢 - 喷油泵问题 - 机油供应问题 - 低油压 - 增压器问题 - 气门问题 解决办法： - 降低负载 - 如果海拔超过1000米，对发动机进行相应的调节 - 检查燃油位 - 检查机油 - 检查控制绡 - 检查进气和排气系统 - 排空管路中的空气 - 检查管路接口等 - 检查机油回油管 - 检查进气门开口是否正常 - 外接油箱发动机器确认 - 检查增压器 - 检测外壳进气口 - 机油温度超过70摄氏度是停止加热 - 检查调速器和喷油嘴 - 检测机油泵 - 更换柴油滤清 - 联系经销商 - 联系经销商 - 调节调速器 - 检测喷油泵 - 检测油压 - 清洁，调节或者更换增压器 - 进气口清理 抱歉，系统响应超时，请稍后再试 - 支持中文、英文免费在线翻译 - 支持网页翻译，在输入框输入网页地址即可 - 提供一键清空、复制功能、支持双语对照查看，使您体验更加流畅. <--TOP. 1.15.The engine unable to stop Causes： A. Loose of a semi -- auto safety pipe at connection box. B. Improper contact / break of circuit. C. Faults on stop button. D. Faults on the stop electromagnet. E. Fault on the fuel closing valve. F. Block of the oil return pipe. Remedies： A. Press the button of the safety pipe for reset of the pipe. B. Get rid of improper contact / break of circuit; check oxidation of joints, clean if necessary. C. Replace the stop button. D. Check / replace the stop electromagnet. E. Shown on "Possible Fault on fuel closing valve". F. Check block, torsion, or dent of oil return pipe.. 1.15引擎无法停止 原因分析： A .松散的半——汽车安全管连接盒。 B .不当联系/线路断线。 C .故障停机按钮。 D .故障停止电磁铁。 E .故障的燃料关闭阀。 F .块回油管。 解决办法： A按按钮复位安全管的管。 B .摆脱不当联系/线路断线；检查氧化接头，必要时进行清洗。 C取代停止按钮。 D.检查/更换站电磁铁。 E .证明“可能的故障的燃料关闭阀”。 F .校验块，扭转，或凹陷油回流管。 <--TOP. 1.16.The engine cannot reach the rated rotary speed Causes： A. Too large load considering of rated power. B. Problems concerning the tachometer. C. Improper adjust of the control rod of throttle. D. Block of oil suction pipe. E. Fault of speed adjustor or improper setup. F. Too low max. speed limit of the speed adjustor. G. Water in fuel. Remedies： A. Decrease load or adopt low grades. B. Check with a manual tachometer or the digital tachometer. C. Check the stroke of throttle. D. Check block of oil suction pipe, replace if necessary. E. Check /adjust the speed adjustor. F. Check /adjust the speed adjustor. G. Replace fuel, install oil and water separator.. 1.16.引擎无法达到额定转速 原因分析： A.太大载荷额定功率。 B .有关问题的转速表。 C .不当调整油门控制杆。 D块吸油管。 E .故障或安装不当速度调节器。 F .太低，最高速度限制的速度调节器。 G .水在燃料。 解决办法： A .降低负载或采用低年级。 B .检查手动或数字转速表转速表。 C.检查行程节流阀。 D.检查块吸油管，必要时更换。 E.检查/调整速度调节器。 F .检查/调整速度调节器。 G .替代燃料，安装油水分离器。 <--TOP. 1.17.Emitting blue smoke or white smoke Causes: A. Applied wrong type of lub. Oil. B. Faults on the cooling start system. C. Too low temperature of engine. D. Excess lub. Oil of engine. E. Wear of sealing ring &bearing of turbocharger. F. Applied wrong type or brand of fuel. G. Close to overhaul limit of engine. H. Water leakage of cylinder end. Remedies: A. Replace lub. Oil and filter/ ensure application of correct type of lub. Oil. B. Install the cooling start set, check, repair, if necessary replace. C. Shown on "the temp.of coolant below the normal temperature". D. Check the level of lub. Oil. E. Repair/ replace turbocharger. F. Apply a temporary oil tank to start engine for identification. G. Overhaul of engine. H. Check cylinder end and liner, if necessary, replace.. 1.17.排放蓝色或白色烟雾 原因分析： A .适用错误类型的润滑油。 B .对冷启动系统。 C .太低温发动机。 D .多余的润滑。发动机机油。 E磨损密封环和轴承的涡轮增压器。 F .应用错误的类型或品牌的燃料。 G .接近极限的发动机大修。 E.水泄漏的气缸头。 解决办法： A .更换润滑。油过滤器/保证应用正确类型的润滑。油。 B .安装冷却开始设置，检查，必要时修理，更换。 C .显示在“temp.of冷却低于正常温度”。 D .检查水平滑。油。 E .修理/更换涡轮增压器。 F .申请临时油罐启动发动机鉴定。 G .发动机大修。 H .检查气缸端和班轮，如果有必要，取代。 <--TOP. 1.18.Emitting black smoke Causes: A. Block of the air inlet system. B. Faults on the fuel injector or wrong type of the injector. C. Faults on the cool start system. D. Apply wrong type or brand of fuel. E. Block of the exhaust pipe. F. Too low temperature of engine. G. Improper gap of air door. H. Air leakage Of the inlet pipe between turbocharger and cylinder cover. I. Block of oil return pipe. J. Thin air owing to too high ambient temp. or altitude. K. Improper timing of oi1 supply. Remedies: A. Check if there is a b1ock of the air inlet system. B. Check/adjust or replace the fuel injector. C. Install the cool start set, check, repair, and if necessary replace. D. Apply a temporary oil tank to start engine for identification. E. Check if the exhaust pipe is blocked, and its size. F. Shown on "the temp. of coolant below the normal temperature". G. Adjust gap of air door. H. Check block of oil return pipe. I. Check block, torsion, or dent of oil return pipe. J. Modification as per the methods stipulated in the sales manual of engine. K. Check data of the oil injection pump, and adjust.. 1.18.冒黑烟 原因分析： A进气系统堵塞。 B .故障的燃料喷射器或错型注射器。 C .对冷启动系统。 D .运用错误的类型或品牌的燃料。 E块的排气管。 F .太低温发动机。 G .不当的差距空气门。 H .漏风的入口管之间的涡轮增压器和气缸盖。 I.回油管堵塞。 J .稀薄的空气由于环境温度太高。或高度。 K .时机不当供油。 解决办法： A.检查是否有一个阻滞的进气系统。 B .检查/调整或更换喷油器。 C安装冷启动，检查，修理和更换，如果必要的话。 D .申请临时油罐启动发动机鉴定。 E.检查如果排气管堵塞，和它的大小。 F .显示在“临时。冷却低于正常温度”。 G .调整间隙空气门。 H .校验块回油管。 I.校验，扭转，或凹陷油回流管。 J .修改按方法中规定的发动机销售手册。 K.光检查数据的注油泵，并调整。 翻译结果重试 抱歉，系统响应超时，请稍后再试 - 支持中文、英文免费在线翻译 - 支持网页翻译，在输入框输入网页地址即可 - 提供一键清空、复制功能、支持双语对照查看，使您体验更加流畅 <--TOP. 1.19.The engine can start but cannot keep running Causes: A. There is air inside the fuel oil system. B. Leakage or block of the fuel system. C. Gearing between the driving set and the engine. D. Block of the fuel filter or freeze of fuel owing to too low temperature. E. Block of oil suction pipes. F. Apply wrong type or brand of fuel oil. G. Water in fuel oil. H. Insufficient preheating. I. Block of air inlet system. J. Damage of pressure pipe. Remedies: A. Remove air inside the fuel oil; tighten joints of oil pipes and the filter. B. Check the vertical pipes of the oil tank. C. Decoupling the driving set of the engine. D. Replace the fuel filter and add a heater for fuel. E. C1ean pipes. F. Adopt a temporary oil tank to start engine for identification. G. Replace fuel oil, install a oil and water separator. H. Consult the user’s manual or check the safety pipe, press button for reset if necessary, inspect wire, locked button, preheating relay. Contact with the authorized for replace of the preheating parts. I. Clean air inlet pipes. J. Install a new pressure pipe. 1.19.发动机能起动而不能继续运行 原因分析： A.内有空气燃料油系统。 B .泄漏或块的燃料系统。 C.之间的传动装置和发动机。 D.柴油滤清堵塞或冻结燃料由于温度太低。 E块吸油管。 F .运用错误的类型或品牌的燃料油。 G .水在燃料油。 H .预热不足。 I.空气进气系统堵塞 J .破坏压力管。 解决办法： A.去除空气内的燃料油；拧紧接头油管道和过滤器。 B .检查垂直管的油箱。 C .解耦驱动的发动机。 D .更换燃油过滤器和添加燃油加热器。 E .清洁油管管。 F .采取临时油罐启动发动机鉴定。 G .替代燃料油，安装油水分离器。 H .查阅用户手册或检查保险管，按下按钮复位，如果必要，检查电线，锁定按钮，预热继电器。与授权代替预热部分。 I.清洁空气入口管。 J .安装一个新的压力管。 翻译结果重试 抱歉，系统响应超时，请稍后再试 - 支持中文、英文免费在线翻译 - 支持网页翻译，在输入框输入网页地址即可 - 提供一键清空、复制功能、支持双语对照查看，使您体验更加流畅. <--TOP. 1.20.May turn the engine but cannot start, without smoke from the exhaust pipe Causes: A. No oil in the fuel box. B. Faults on the electromagnet for stop. C. Faults on the fuel closing valve. D. No oil injected from the oil injector. E. Loose of joints of oil suction pipe of oil transfer pump. F. Block of the fuel filter or block of the oil suction pipe. G. No oil inside the oil pump. H. Block of air inlet or outlet system. I. Break of the driving axle of the pump. J. Damage of gear pump or wear of gear. K. Faults on the oil transfer pump. L. Block of the jet of the oil injector Remedies: A. Fill fuel oil. B. Check the electromagnet and replace it if necessary. C. Shown on "possible faults on closing valve". D. Loose the oil pipe between the oil injection pump and the cylinder cover, start the engine to see if there is a leakage. E. Tighten all pipe joints of the filter between oil tank and oil pump. F. Replace fuel filter, check if flexible pipe is blocked. G. Pump oil by the feeding pump. H. Cheek if there are blocks of air inlet or air inlet or outlet system. I. Contact with the agent. J. Contact with the agent. K. Check/repair the oil transfer pump, replace it if necessary. L. Check/clean or replace the injector. 1.20.引擎无法启动，无烟雾从排气管 原因分析： A.燃油用尽。 B .故障对电磁铁停止。 C .故障的燃料关闭阀。 D .无油注入从喷油器。 E .松散的关节吸油管输油泵。 F .块燃料过滤器或块吸油管。 J.油泵。 H .块空气入口或出口系统。 M.打破的驱动轴泵。 J .损坏或磨损的齿轮泵齿轮。 K.对油输送泵。 M.喷油嘴堵塞 解决办法： A .填补燃料油。 B .检查电磁铁，必要时予以更换。 C .显示在“可能的故障关闭阀”。 D .松开油管与油泵，气缸盖，启动发动机，看看是否有渗漏。 E.拧紧所有管接头的过滤器之间的油箱和油泵。 F .更换燃油滤清器，检查是否灵活管堵塞。 G .泵油的输送泵。 H .若有块空气入口和空气入口或出口系统。 I.与代理联系。 J .与代理联系。 K.检查/修复输油泵，必要时予以更换。 L .检查/清洁或更换喷油器。 翻译结果重试 抱歉，系统响应超时，请稍后再试 - 支持中文、英文免费在线翻译 - 支持网页翻译，在输入框输入网页地址即可 - 提供一键清空、复制功能、支持双语对照查看，使您体验更加流畅. <--TOP. 1.21.The engine has the start difficulty or cannot start, gives off black smoke Causes: A. Too low speed of the start motor driving the engine. B. Gearing of the driving set and the engine. C. Mistakenly apply cold start set. D. Insufficient preheating. E. Block of the fuel oil filter. F. Air in the fuel system. G. Block of oil suction pipes. H. Block of air inlet system. I. Water in the fuel oil. J. Apply wrong type or brand of fuel oil. K. Fault of oil injector or wrong type of the injector. L. Loose of pipe joints of oiI inlet, oil return of the injector. M. Fau1t of the oil delivery pump. N. Fault of the oil injection pump. O. Wrong timing of oil supply. P. Wrong valve timing. Q. Low compressed pressure. R. Block of fuel closing valve. S. Block of the exhaust pipe. Remedies: A. Shown on "unable to turn engine or too low turn speed". B. Decoupling of the driving set. C. Refer to the user’s manual for how to operate the cold start system. D. Consult the user’s manual or check the semi-auto safety pipe, press button for reset if necessary, inspect wire, locked button, preheat relay. Contact the authorized for replace of the preheat parts. E. Replace the fuel oil filter. F. Remove the air. G. Clean the oil suction pipes. H. Clean the air inlet pipes. I. Replace fuel, add a oil and water separator. J. Adopt a temporary oil tank to start the engine. K. Implement pressure test/ adjust or replace the injector. L. Tighten the pipe joints. M. Check/ repair the pump, replace if necessary. N. Ask the agent to check the pump. O. lnspect the data of the pump and adjust. P. Adjusted as per the sipulated data. Q. Shown on"low of compressed pressure". R. Shown on"possible faults on the fuel closing valve". S. Check if the exhaust pipes blocked.. 1.1.21.发动机启动困难或不能启动，发出黑烟 原因分析： A.很低的速度的启动电机驱动发动机。 B .传动的驱动装置和发动机。 C .误将冷启动设置。 D .预热不足。 E块燃料油过滤器。 F .燃料空气系统。 G .块吸油管。 H .块的进气系统。 I.燃料油中有水分 J .运用错误的类型或品牌的燃料油。 K故障喷油器或错型注射器。 L.松散的管接头油口，回油注射器。 M.的输油泵故障。 N.油泵的故障。 O .错误的时机石油供应站。 P .错配。 Q.低的压缩压力。 R块燃料关闭阀。 S排气管堵塞。 解决办法： A.显示“无法转动发动机或太低转速度”。 B .解耦的驱动装置。 C .参阅用户手册如何操作冷启动系统。 D .查阅用户手册或检查的半自动安全管，按下按钮复位，如果有必要，检查电线，锁定按钮，预热继电器。联系授权代替预热部分。 E .代替燃料油过滤器。 F .消除空气。 G .清洁吸油管。 H .清洁空气入口管。 I.替代燃料，添加一个油水分离器。 J .采取临时油罐启动发动机。 K .实施压力测试/调整或更换喷油器。 L拧紧管接头。 M .检查/维修水泵，必要时更换。 N.要求代理人检查泵。 O .检验数据的泵和调整。 P调整为每数据页。 Q.在“低压缩压力”。 R.河上“可能的故障的燃料关闭阀”。 S.检查排气管堵塞。 翻译结果重试 抱歉，系统响应超时，请稍后再试 - 支持中文、英文免费在线翻译 - 支持网页翻译，在输入框输入网页地址即可 - 提供一键清空、复制功能、支持双语对照查看，使您体验更加流畅 <--TOP. 1.22.The engine cannot be turned or only be turned slowly Causes: A. Insufficiently charged of the battery. B. Break of main switch. C. loose of a semi -- auto safety pipe at the connection box. D. Improper contact or break of circuit. E. Faults of the key switch. F. Faults of the start relay. G. Faults of the start motor. H. Faults of any start circuit. I. Water inside the engine. J. Low temperature of lubricant oil. K. Apply wrong type of lub. Oil. L. Other inside and outside causes affecting turn of the engine. Remedies： A. Check the electrolyte level and add if necessary. Charge the storage battery, replace it if necessary. B. Close the main switch. C. Press the button at the pipe for reset. D. Remove any break or improper contact, check if there is oxidation, wash if necessary. E. Replace the key switch. F. Replace the start relay. G. Contact the authorized personnel. H. Check all other start circuit. I. Contact with the authorized repairman, donˉtry to start the engine. J. Install the lub. Oil heater at the bottom. K. Replace lub. Oi1 and the filter or ensure correct type of lub. Oil. L. Check if the crank is flexible. 1.22.引擎无法停机或者停机很慢 原因分析： A.电池的充电不足。 B .打开主开关。 C .松散的半——汽车安全管在连接盒。 D .接触不良或断开电路。 E .故障的按键开关。 F .故障继电器的。 G .故障启动马达。 H .任何启动电路故障。 I引擎进水。 J .低温润滑油。 K .申请错误类型的润滑。油。 L其他内部和外部原因影响转向发动机。 解决办法： A.检查电解质水平和添加如果需要。 电瓶充电，必要时予以更换。 B .关闭主开关。 C .按下按钮在管复位。 D .消除任何中断或接触不良，检查是否有氧化，如果必要洗。 E .更换钥匙开关。 F .更换启动继电器。 G .联系人员的授权。 H .检查所有其他启动电路。 I.授权的修理工，不ˉ尝试启动发动机。 J .安装滑。油加热器底部。 K .更换润滑。油过滤器或确保正确类型的润滑。油。 L .检查曲柄灵活。 翻译结果重试 抱歉，系统响应超时，请稍后再试 - 支持中文、英文免费在线翻译 - 支持网页翻译，在输入框输入网页地址即可 - 提供一键清空、复制功能、支持双语对照查看，使您体验更加流畅 <--TOP 2、ALTERNATOR. 2.1 Too low voltage of the genset under a load A. Check if the rotary speed of the genset is normal. B. Check if the UFRO set of AVR is correct. C. As per the test of excitation separation, check AVR. D. Damage of rotary diode. 2. 电机部分 2.1电压太低的机组负荷下 检查如果旋转速度是正常的。 B .检查是否电压掉解气ufro集单片机是否正确。 C .根据测试激励分离，检查系统。 D .损坏旋转二极管 <--TOP 2.2 Too low voltage at free running of the genset A. Check if the rotary speed of the genset is too low. B. Check if l -- 2 connection of AVR or outside connected manual micro adjustment is perfect.. 2.2电压太低在自由运行的发电机组 A.检查如果旋转速度电流太低。 B .看看我——2连接单片机或外接手动微调是完美的。 <--TOP 2.3 Too High of Output Voltage A. Check if the rotary speed of the genset is too high. B. Check if the load of the genset is of capacitive load (leading power factor). 2.3输出电压太高 A.检查如果旋转速度太高的发电机组。 B .检查是否负荷机组的电容性负载（领先的功率因数） <--TOP 2.4 Unstable Output of Voltage of the Genset A. Check if the rotary speed is stable. B. Check if the setup of stability is correct. 2.4不稳定输出电压的发电机组 A.检查如果旋转速度稳定。 B .检查是否安装正确的稳定性。 <--TOP 2.5 During running of the genset, no voltage outputs A. Check the connection ofK1 -- K2 from AVR is correct and reliable. B. Check the rotary speed of the diesel genset. C. Check the residual magnetism voltage, charge magnetism if necessary. D. As per the test of excitation separation, check alternator and AVR. 2.5在运行的发电机组，无电压输出 A.检查连接ofk1——幼器是正确的和可靠的。 B .检查旋转速度的柴油发电机组。 检查剩磁电压，如果必要的充磁。 D .根据测试激励分离，检查发电机和稳压器。 3.Electrical Control. 3.1 Remote Emergency Stop Cannot Be Realized A. Confirm the remote contact was normally realized. B. Confirm the CV2 agreed adaptor was installed in 550, with correct connection. C. Confirm CV2 related connection wires are correct free of miss. D. Confirm the genset is of auto standby mode. E. Confirm the secrete remote codes input correctly. <--TOP 3电气部分 3.1无法实现远程紧急停车 A .确认远程接触通常是实现。 B .确认C V2同意适配器是安装在550，与正确的连接。 C .确认C V2相关连接线是正确的自由小姐。 D .确认机组自动待机模式。 E .确认分泌遥控码输入正确。 3.2. Remote Monitor Cannot Be Realized A. Confirm the monitor software is correctly installed in a remote PC. B. Confirm the setting of contact parameters of monitor interface correctly , corresponding with the actual connection modes. C. In case of contact of dialing numbers, confirm the MODEM correctly tested by 550, confirm correct settings of remote MODEM. D. Confirm contact circuit correct and reliable, free of busy. E. Confirm the contact interface correctly connected with the contact module. <--TOP 3.2。远程监控是无法实现的 A .确认监控软件是正确安装在远程电脑。 B .确认设置的接触参数的监控界面，与相应的实际接线方式。 C .万一接触拨号调制解调器，确认正确测试550，确认正确设置远程调制解调器。 D .确定联络电路正确和可靠的，免费的忙。 E .确认连接正确的接触界面接触模块。 3.3.The genset unable to stop automatically in the auto mode A. Confirm the public power resumes normal completely. B. Confirm there is no actions of public power inductor. C. Confirm completion of delay of auto stop. D. Check if the magnetic valve of fuel is normal, replace if necessary. E. For the genset with the electronic speed adjusting system, confirm all EPG settings are correct and reasonable. F. Confirm correct settings of oil volume of oil injection pump. <--TOP 3.3.机组无法自动停止自动模式 A .确认公共权力完全恢复正常。 B .证实是没有行动的公共功率电感。 C .确认完成延迟自动停止。 D .检查电磁阀的燃料是正常的，必要时更换。 E.用于发电机组的电子调速系统，确认所有的电子节目指南设置是正确的，合理的。 F .确认正确设置油量的油泵。 3.4. Unable to stop manually A. Inspect the positions of key switch and control switch are correct. B. , , Co, nfirm all ele, ctri, , cal control parts are normal. C. Inspect if the magnetic valve of fuel is normal, replace if necessary. D. For the genset with the electronic speed adjusting system, confirm all EPG , settings are correct and reasonable. E. Confirm correct setting of oil volume of oil injector. F. For 550, confirm the genset runs , man, , ually. 3.4。无法停止手动 A.检查的立场关键开关和控制开关是正确的。 B，，公司确认，全要素，ctri，，控制部分是正常的。 C.检查如果电磁阀的燃料是正常的，必要时更换。 D .为发电机组的电子调速系统，确认所有的电子节目指南，设置是正确的，合理的。 E .确认正确设置油量的油喷射器。 F .550，确定机组运行，，，等。 3.5. The genset unable to undertake load A. Check if the voltage is normal. B. Check features of load, confirm free of overload and leading power factor. C. Confirm the handle of MCCB upwards and set of all items are correct and reasonable. D. For clients equipped with ATS, especially inspect ATS and relevant parts. E. Inspec, t all connection wires controlled by ATS, ensure there is no mistakes. F. Confirm ATS transfer control switch isn’t at the"MAINS" position. G. In case of A, TS transfe, r control , switch away of the"AUTO" position, confirm the connected public power without normal voltage. H. Confirm the power of the genset , correctly connected with ATS terminals. I. Confirm the main AC contactor of ATS flexible, without block. <--TOP 3.5。发电机组不能承担负荷 A.检查电压是否正常。 B .检查负载特点，确认无过载和领先的功率因数。 C .确认手柄上设置塑壳断路器的所有项目都是正确的，合理的。 D .为客户配备了自动测试系统，着重考察及相关配件。 体育中心，所有的连接线控制系统，确保没有错误。 F .确认测试传输控制开关不在“电源”的位置。 G .情况的一个指标，分析，控制，开关的“自动”位置，确认连接公共权力不正常电压。 阁下确认电源的发电机组，自动正确连接终端。 我确认主交流接触器自动测试系统的柔性，无块 3.6. Low Voltage Alarming A. Measure the actual value of voltage output of the genset. B. Confirm there is no deflection on meter indication. C. In case of low actual voltage, inspect as procedures and readjust AVR. D. Confirm normal rotary speed /frequency. E. In case of normal actual voltage, check if the circuit for display of voltage is correct. F. Especially inspect the three fuses are normal and connected reliably. G. Confirm there is no big variant of three phases of voltage. H. Confirm there is no miss of phase. I. Confirm in case of alarming, there is no big variant of load. J. Confirm the genset runs without overload. K. For 550 electrical control systems, check if the alarming limit of low voltage is reasonable. 3.6。低电压报警 A.衡量实际电压值输出的发电机组。 B .确认有无挠度计指示。 C .在低实际电压，检查程序和调整器。 D .确认正常的旋转速度/频率。 在正常情况下的实际电压，检查是否显示电路的电压是正确的。 F .特别检查三保险丝正常、可靠的连接。 G .确认有无大变异的三个阶段的电压。 H .确认有无缺相。 我确认在案件报警，也没有大变负荷。 J .确认机组运行不超载。 K .550电气控制系统，检查是否是合理的限制低电压报警。 翻译结果重试 抱歉，系统响应超时，请稍后再试 - 支持中文、英文免费在线翻译 - 支持网页翻译，在输入框输入网页地址即可 - 提供一键清空、复制功能、支持双语对照查看，使您体验更加流畅 3.7. High Voltage Alarming A. Measure the actual value of vo, ltage output of the genset. B. Confirm there is no deflection on meter indication. C. In case of high of actua1 voltage, inspect as procedures and readjust AVR. D. Confirm free of capacitive load and leading power factor. E. Confirm normal rotary speed/frequency. F. In case of normal actual vo, ltage, check if the circuit for display of voltage is correct. G. For 550 electrical control system, check if the alarming limit of high voltag, e is r, easonable 3.7。高电压报警 A.衡量实际价值的旁白，ltage输出电流。 B .确认有无挠度计指示。 在案件高的实际电压，检查程序和调整器。 D .确认无容性负载和领先的功率因数。 E .确认正常的旋转速度/频率。 F .正常情况下的实际旁白，ltage，检查是否显示电路的电压是正确的。 G .550电气控制系统，检查是否报警限制高电压，是的，合理的 3.8. Stop Of Over Speed Fault A. Check if there is an abnormal indication of the tachometer. B. For the mechanical speed adjusting mechanism, check if the pull -- rod of throttle is flexible, and ensure correct adjustment. C. For the electronic speed adjusting system, check if the pull -- rod of thrott1e is flexible and if the act mechanism acts correctly, and ensure correct adjustment of EPG. D. Realignment and adjustment of limit of over speed protection. E. For 50l, 520 electrical control system, check the position of micro switch behind is correct. F. For 550 electrical control system, check if the stop of over speed protection is set reasonable. G. After removal of faults, reset the a1arming signal on the control panel. <--TOP 3.8。停止超速故障 A.检查是否有异常迹象的转速表。 B机械调速机构，检查是否拉——杆油门是灵活的，并确保正确的调整。 C .为电子调速系统，检查是否拉——杆thrott1e是灵活的，如果正确行为机制的行为，并确保正确的调整方法。 D .调整和调整限制超速保护。 E520电气控制系统的位置，检查微动开关的背后是正确的。 F .550电气控制系统，检查如果停止超速保护是合理的。 G .后清除故障，a1arming重置信号的控制面板。 3.9. Low Oil Pressure Faults Alarming/Stop A. Check the level of engine oil. B. Check quality, and viscosity of engine oil. C. Check the temperature of engine oil. D. Check if the sensor of oil pressure is damaged. E. For 50l, 520 electrical control systems, check the position of micro switch behind is correct. F. For 550 electrical control system, check if the low oil temp. alarming/stop is set reasonable. G. Check if the filter of engine oil and oil passage are blocked. <--TOP 3.9。机油压力低故障报警/停止 A .检查机油液位。 B .检查质量，和粘度的机油。 检查机油温度。 检查如果传感器油压力损坏。 EL，520电气控制系统的位置，检查微动开关的背后是正确的。 F .550电气控制系统，检查是否低油温。报警/停止是合理的。 G .检查如果滤清器机油和油路堵塞。 3.10. High Water Temperature Faults Alarming/Stop A. Check if the genset is overload. B. Check if the heat radiator is blocked. C. Check the tightness of the belt of fan. D. After complete cooling of the genset, check if the level of cooling water is enough. E. Check if the water temperature sensor is damaged. F. For 50l, 520 electrical control systems, check the position of micro switch behind is correct. G. For 550 electrical control systems, check if the high water temp. alarming/stop is set reasonable. H. Check if the thermostat can be opened correctly. I. Check if the gap of water tank and water pump is correct. J. Ensure the temp. inside the room no more than 40 <--TOP 3.10。高水温故障报警/停止 A.检查如果机组过载。 B .检查散热器的热阻塞。 C.检查皮带松紧的风扇。 D.后完全冷却发电机组的水平，检查冷却水是足够的。 E.检查如果水温传感器损坏。 F.为520L，电气控制系统，检查的立场，微动开关后面是正确的。 G .550电气控制系统，检查是否高水温。报警/停止是合理的。 H .检查是否可以正确打开恒温器。 我检查如果差距的水箱和水泵是正确的。 J .确保温度。房间内不超过40 翻译结果重试 抱歉，系统响应超时，请稍后再试 - 支持中文、英文免费在线翻译 - 支持网页翻译，在输入框输入网页地址即可 - 提供一键清空、复制功能、支持双语对照查看，使您体验更加流畅 3.11. In case of the start motor running, the genset unable to couple A. Check fue1 level, ensure correct connection of oil pipe. B. For the genset with mechanical speed adjusting system, checks if the magnetic valve of throttle is correctly suctioned. C. For the genset with electrical speed adjusting system, checks if EPG power is correctly connected and if the voltage is normal. D. For the genset with electrical speed adjusting system, in the course of start motor running, check if there is a correct AC voltage signal at MPU. E. Check if the rotary speed of the genset reached or excelled the set normal rotary speed for start. F. Check if the fuel transfer system is blocked. G. Check if the air filter is blocked. H. At the cold areas, before start, ensure the genset is preheated 3.11. 在起动马达运行情况下，机组无法启动 A。 检查燃油水平，保证油管的正确连接。 B. 为动力调整系统的机械速度，检查节流孔磁性阀门是否正确地匹配。 C. 为机组调整系统的电子速度，检查 EPG是否正确地连接，电压是否正常。 D. 为机组调整系统的电子速度，起动马达启动时，是否有一个正确交流电压信号在主处理机。 G. 检查空气过滤器是否堵塞。 H. 在寒冷地带，启动之前，保证机组被预先加热 <--TOP 3.12. In case of the signal"START" correctly input, but manual /auto unable to start A. Check if the emergency stop button is free. B. Check if the control key is at the position of "STOP". C. Check if there is fault indication, repair faults if necessary, and reset relevant information. D. Check the battery voltage, in case of too low voltage, recharges the battery fully. In case of normal voltage, as per drawings, step by step check the voltage signal is correctly delivered to all control points such as magnetic valve of throttle and start motor, etc. E. In case of all outside connections without problems , replace re1evant electrical control unit 3.12启动信号输入之后，机组为启动 A．检查急停开关是否弹起 B.检查控制开关是否在关的位置 C. 是否有问题指示灯亮起，若有，检查设置。输入正确数据 D.检查电瓶电量是否充足，不足的话充满电瓶。检查接线，确认电压输出信号正常。 E. 外部接线全部正常故障扔为排除，重新连接控制系统电路 <--TOP 3.13. In case of key turned to"START", the genset unable to star A. Check if the key switch moves correctly. B. Check if there is fault indication, repair faults if necessary, and reset relevant information. C. Check the battery voltage, in case of too low voltage, recharge the battery fully. In case of normal voltage, as per drawings, step by step check the voltage signal is correctly delivered to all control points such as magnetic valve of throttle and start motor, etc. D. Check if the emergency stop button is free. <--TOP 3.13 钥匙转到“启动” 开关时，设备无法启动 A.确认启动钥匙方向正确 B.检查设备无故障 C. 检查电瓶电量是否充足，不足的话充满电瓶。检查接线，确认电压输出信号正常 D. 检查急停开关是否弹起